## Sheet1
Draft: Assessment of TP Load Removal Requirements at GWP
Shafer: June 23, 2015
2008-2012 Average Annual Inflow Cntrol 2 |  |  |  | 44885.9504 | ac-ft
Total Load at Control 2 (assume TP concentration of 0.10 mg/L) |  |  |  | 5540.8547 | kg/yr TP
Flow (cfs) | Flow (ac-ft/yr) | Flow (M3) | Inflow Conc (mg/L) | Outflow Conc. At Cntrol 4 (mg/L) | Total Load Retained (kg/yr)
62 | 44885.9504 | 55408547.4674 | 0.1 | 0.08 | 1108.1709
62 | 44885.9504 | 55408547.4674 | 0.1 | 0.06 | 2216.3419
62 | 44885.9504 | 55408547.4674 | 0.1 | 0.04 | 3324.5128
35 | 25338.843 | 31279018.7316 | 0.1 | 0.04 | 1876.7411
97 | 70224.7934 | 86687566.199 | 0.1 | 0.04 | 5201.254
Q existing | 62 | cfs
Addl Q | 35 | cfs
Assuming that GWP outflow concentration is 0.040 mg/L, the total load delivered to GWP
is approximately 3,300 kg/yr. With project, the total load would be 5,200 kg/yr. So must
remove 2,100 kg/yr. This should be done upstream of GWP or by diversion around it.)
Using Kadlec Eqn K-C* (1996) we can compute how much load would be removed by
a 1,400 acre impoundment assuming an effluent concentration of 20 ppb.
Area = Q/k* Ln ((Co-c*)(Ci-C*))
Where:
| Q (cfs) | 35
| Q (m3/yr) | 31279018.7316 | M3/yr
| Ci | 0.1 | mg/L
| Co | 0.02 | mg/L
| C* | 0.01 | mg/L
| K | 12 | m/yr
| Area | 572.7252 | hectares
| Area | 1415.2327 | acres
| Load Removal | 2502.3215 | kg/yr
Without Condition
| Q = | 62
| TP Load | #REF!
| Q = | 97
| TP Load | #REF!